## RW_HOLDING_REGISTER
No. | DCS WRITE HOLDING REGISTERS
| LABEL | PLC ADDRESS HANDSHAKE |  |  |  | MODBUS ADDRESS |  | TYPE | RANGE
|  | DCS | BAT |  |  | DCS | BAT
1 | AO_ModeChoice | D0000 | D0020 | CIO | 300 | 400001 | 400021 | Int(16) | Auto=1/REM=2/LOCAL=3/BAT=4
2 | AO_MDrainTimeSet | D0001 | D0021 | CIO | 301 | 400002 | 400022 | Int(16) | 1-1800
3 | AO_AHDrainTimeSet | D0002 | D0022 | CIO | 302 | 400003 | 400023 | Int(16) | 1-1800
4 | AO_TimeSet_IK1 | D0003 | D0023 | CIO | 303 | 400004 | 400024 | Int(16) | 10-200
5 | AO_TimeSet_IK2 | D0004 | D0024 | CIO | 304 | 400005 | 400025 | Int(16) | 10-200
6 | AO_ManCode_L | D0005 | D0025 | CIO | 305 | 400006 | 400026 | Int(16) | 101-902 ==>pointer where to start
7 | AO_ManCode_R | D0006 | D0026 | CIO | 306 | 400007 | 400027 | Int(16) | 101-902 ==>pointer where to start
8 | AO_AHTimes | D0007 | D0027 | CIO | 307 | 400008 | 400028 | Int(16) | 1-40
9 | AO_Seq1 | D0008 | D0028 | CIO | 308 | 400009 | 400029 | Int(16) | 0-9
10 | AO_Seq2 | D0009 | D0029 | CIO | 309 | 400010 | 400030 | Int(16) | 0-9
11 | AO_Seq3 | D0010 | D0030 | CIO | 310 | 400011 | 400031 | Int(16) | 0-9
12 | AO_Seq4 | D0011 | D0031 | CIO | 311 | 400012 | 400032 | Int(16) | 0-9
13 | AO_Seq5 | D0012 | D0032 | CIO | 312 | 400013 | 400033 | Int(16) | 0-9
14 | AO_Seq6 | D0013 | D0033 | CIO | 313 | 400014 | 400034 | Int(16) | 0-9
15 | AO_Seq7 | D0014 | D0034 | CIO | 314 | 400015 | 400035 | Int(16) | 0-9
16 | AO_Seq8 | D0015 | D0035 | CIO | 315 | 400016 | 400036 | Int(16) | 0-9
17 | AO_Seq9 | D0016 | D0036 | CIO | 316 | 400017 | 400037 | Int(16) | 0-9

## READ DISCRETE INPUT
No. | DCS READ DISCRETE INPUTS
| LABEL | PLC ADDRESS | MODBUS ADDRESS | DESCRIPTION | TYPE
FURNACE WALL (FRONT)
1 | DI_bypassed_101 | 27804 | 104453 | 10HCB11 AT001 bypassed | Binary
2 | DI_bypassed_102 | 27805 | 104454 | 10HCB11 AT002 bypassed | Binary
3 | DI_bypassed_103 | 27806 | 104455 | 10HCB11 AT003 bypassed | Binary
4 | DI_bypassed_104 | 27807 | 104456 | 10HCB11 AT004 bypassed | Binary
5 | DI_bypassed_105 | 27808 | 104457 | 10HCB11 AT005 bypassed | Binary
6 | DI_bypassed_106 | 27809 | 104458 | 10HCB11 AT006 bypassed | Binary
7 | DI_bypassed_107 | 27810 | 104459 | 10HCB11 AT007 bypassed | Binary
8 | DI_bypassed_108 | 27811 | 104460 | 10HCB11 AT008 bypassed | Binary
9 | DI_bypassed_109 | 27812 | 104461 | 10HCB11 AT009 bypassed | Binary
10 | DI_bypassed_110 | 27813 | 104462 | 10HCB11 AT010 bypassed | Binary
11 | DI_bypassed_111 | 27814 | 104463 | 10HCB11 AT011 bypassed | Binary
12 | DI_bypassed_112 | 27815 | 104464 | 10HCB11 AT012 bypassed | Binary
13 | DI_bypassed_113 | 27900 | 104465 | 10HCB11 AT013 bypassed | Binary
14 | DI_bypassed_114 | 27901 | 104466 | 10HCB11 AT014 bypassed | Binary
15 | DI_bypassed_115 | 27902 | 104467 | 10HCB11 AT015 bypassed | Binary
16 | DI_bypassed_116 | 27903 | 104468 | 10HCB11 AT016 bypassed | Binary | NOTE :
17 | DI_bypassed_117 | 27904 | 104469 | 10HCB11 AT017 bypassed | Binary
18 | DI_bypassed_118 | 27905 | 104470 | 10HCB11 AT018 bypassed | Binary | RED | : RETRACT | GREY | : START FAIL
19 | DI_bypassed_119 | 27906 | 104471 | 10HCB11 AT019 bypassed | Binary
20 | DI_bypassed_120 | 27907 | 104472 | 10HCB11 AT020 bypassed | Binary | GREEN | : INSERT/ADVANCE | YELLOW | : READY/STANBY
FURNACE WALL (LEFT)
21 | DI_bypassed_301 | 27700 | 104433 | 10HCB13 AT001 bypassed | Binary
22 | DI_bypassed_302 | 27701 | 104434 | 10HCB13 AT002 bypassed | Binary
23 | DI_bypassed_303 | 27702 | 104435 | 10HCB13 AT003 bypassed | Binary
24 | DI_bypassed_304 | 27703 | 104436 | 10HCB13 AT004 bypassed | Binary
25 | DI_bypassed_305 | 27704 | 104437 | 10HCB13 AT005 bypassed | Binary
26 | DI_bypassed_306 | 27705 | 104438 | 10HCB13 AT006 bypassed | Binary
27 | DI_bypassed_307 | 27706 | 104439 | 10HCB13 AT007 bypassed | Binary
28 | DI_bypassed_308 | 27707 | 104440 | 10HCB13 AT008 bypassed | Binary
29 | DI_bypassed_309 | 27708 | 104441 | 10HCB13 AT009 bypassed | Binary
30 | DI_bypassed_310 | 27709 | 104442 | 10HCB13 AT010 bypassed | Binary
31 | DI_bypassed_311 | 27710 | 104443 | 10HCB13 AT011 bypassed | Binary
32 | DI_bypassed_312 | 27711 | 104444 | 10HCB13 AT012 bypassed | Binary
33 | DI_bypassed_313 | 27712 | 104445 | 10HCB13 AT013 bypassed | Binary
34 | DI_bypassed_314 | 27713 | 104446 | 10HCB13 AT014 bypassed | Binary
35 | DI_bypassed_315 | 27714 | 104447 | 10HCB13 AT015 bypassed | Binary
36 | DI_bypassed_316 | 27715 | 104448 | 10HCB13 AT016 bypassed | Binary
37 | DI_bypassed_317 | 27800 | 104449 | 10HCB13 AT017 bypassed | Binary
38 | DI_bypassed_318 | 27801 | 104450 | 10HCB13 AT018 bypassed | Binary
39 | DI_bypassed_319 | 27802 | 104451 | 10HCB13 AT019 bypassed | Binary
40 | DI_bypassed_320 | 27803 | 104452 | 10HCB13 AT020 bypassed | Binary
FURNACE WALL (RIGHT)
41 | DI_bypassed_401 | 28100 | 104497 | 10HCB14 AT001 bypassed | Binary
42 | DI_bypassed_402 | 28101 | 104498 | 10HCB14 AT002 bypassed | Binary
43 | DI_bypassed_403 | 28102 | 104499 | 10HCB14 AT003 bypassed | Binary
44 | DI_bypassed_404 | 28103 | 104500 | 10HCB14 AT004 bypassed | Binary
45 | DI_bypassed_405 | 28104 | 104501 | 10HCB14 AT005 bypassed | Binary
46 | DI_bypassed_406 | 28105 | 104502 | 10HCB14 AT006 bypassed | Binary
47 | DI_bypassed_407 | 28106 | 104503 | 10HCB14 AT007 bypassed | Binary
48 | DI_bypassed_408 | 28107 | 104504 | 10HCB14 AT008 bypassed | Binary
49 | DI_bypassed_409 | 28108 | 104505 | 10HCB14 AT009 bypassed | Binary
50 | DI_bypassed_410 | 28109 | 104506 | 10HCB14 AT010 bypassed | Binary
51 | DI_bypassed_411 | 28110 | 104507 | 10HCB14 AT011 bypassed | Binary
52 | DI_bypassed_412 | 28111 | 104508 | 10HCB14 AT012 bypassed | Binary
53 | DI_bypassed_413 | 28112 | 104509 | 10HCB14 AT013 bypassed | Binary
54 | DI_bypassed_414 | 28113 | 104510 | 10HCB14 AT014 bypassed | Binary
55 | DI_bypassed_415 | 28114 | 104511 | 10HCB14 AT015 bypassed | Binary
56 | DI_bypassed_416 | 28115 | 104512 | 10HCB14 AT016 bypassed | Binary
57 | DI_bypassed_417 | 28200 | 104513 | 10HCB14 AT017 bypassed | Binary
58 | DI_bypassed_418 | 28201 | 104514 | 10HCB14 AT018 bypassed | Binary
59 | DI_bypassed_419 | 28202 | 104515 | 10HCB14 AT019 bypassed | Binary
60 | DI_bypassed_420 | 28203 | 104516 | 10HCB14 AT020 bypassed | Binary
FURNACE WALL (BACK)
61 | DI_bypassed_201 | 28204 | 104517 | 10HCB12 AT001 bypassed | Binary
62 | DI_bypassed_202 | 28205 | 104518 | 10HCB12 AT002 bypassed | Binary
63 | DI_bypassed_203 | 28206 | 104519 | 10HCB12 AT003 bypassed | Binary
64 | DI_bypassed_204 | 28207 | 104520 | 10HCB12 AT004 bypassed | Binary
65 | DI_bypassed_205 | 28208 | 104521 | 10HCB12 AT005 bypassed | Binary
66 | DI_bypassed_206 | 28209 | 104522 | 10HCB12 AT006 bypassed | Binary
67 | DI_bypassed_207 | 28210 | 104523 | 10HCB12 AT007 bypassed | Binary
68 | DI_bypassed_208 | 28211 | 104524 | 10HCB12 AT008 bypassed | Binary
69 | DI_bypassed_209 | 28212 | 104525 | 10HCB12 AT009 bypassed | Binary
70 | DI_bypassed_210 | 28213 | 104526 | 10HCB12 AT010 bypassed | Binary
71 | DI_bypassed_211 | 28214 | 104527 | 10HCB12 AT011 bypassed | Binary
72 | DI_bypassed_212 | 28215 | 104528 | 10HCB12 AT012 bypassed | Binary
73 | DI_bypassed_213 | 28300 | 104529 | 10HCB12 AT013 bypassed | Binary
74 | DI_bypassed_214 | 28301 | 104530 | 10HCB12 AT014 bypassed | Binary
75 | DI_bypassed_215 | 28302 | 104531 | 10HCB12 AT015 bypassed | Binary
76 | DI_bypassed_216 | 28303 | 104532 | 10HCB12 AT016 bypassed | Binary
77 | DI_bypassed_217 | 28304 | 104533 | 10HCB12 AT017 bypassed | Binary
78 | DI_bypassed_218 | 28305 | 104534 | 10HCB12 AT018 bypassed | Binary
79 | DI_bypassed_219 | 28306 | 104535 | 10HCB12 AT019 bypassed | Binary
80 | DI_bypassed_220 | 28307 | 104536 | 10HCB12 AT020 bypassed | Binary
CONVECTION AREA (LEFT)
81 | DI_bypassed_701 | 27908 | 104473 | 10HCB17 AT001 bypassed | Binary
82 | DI_bypassed_702 | 27909 | 104474 | 10HCB17 AT002 bypassed | Binary
83 | DI_bypassed_703 | 27910 | 104475 | 10HCB17 AT003 bypassed | Binary
84 | DI_bypassed_704 | 27911 | 104476 | 10HCB17 AT004 bypassed | Binary
85 | DI_bypassed_705 | 27912 | 104477 | 10HCB17 AT005 bypassed | Binary
86 | DI_bypassed_706 | 27913 | 104478 | 10HCB17 AT006 bypassed | Binary
87 | DI_bypassed_707 | 27914 | 104479 | 10HCB17 AT007 bypassed | Binary
88 | DI_bypassed_708 | 27915 | 104480 | 10HCB17 AT008 bypassed | Binary
89 | DI_bypassed_709 | 28000 | 104481 | 10HCB17 AT009 bypassed | Binary
90 | DI_bypassed_710 | 28001 | 104482 | 10HCB17 AT010 bypassed | Binary
91 | DI_bypassed_711 | 28002 | 104483 | 10HCB17 AT011 bypassed | Binary
92 | DI_bypassed_712 | 28003 | 104484 | 10HCB17 AT012 bypassed | Binary
93 | DI_bypassed_713 | 28004 | 104485 | 10HCB17 AT013 bypassed | Binary
94 | DI_bypassed_501 | 28005 | 104486 | 10HCB15 AT001 bypassed | Binary
95 | DI_bypassed_502 | 28006 | 104487 | 10HCB15 AT002 bypassed | Binary
96 | DI_bypassed_503 | 28007 | 104488 | 10HCB15 AT003 bypassed | Binary
97 | DI_bypassed_504 | 28008 | 104489 | 10HCB15 AT004 bypassed | Binary
98 | DI_bypassed_901 | 28009 | 104490 | 10HCB19 AT001bypassed | Binary
CONVECTION AREA RIGHT)
99 | DI_bypassed_801 | 28308 | 104537 | 10HCB18 AT001 bypassed | Binary
100 | DI_bypassed_802 | 28309 | 104538 | 10HCB18 AT002 bypassed | Binary
101 | DI_bypassed_803 | 28310 | 104539 | 10HCB18 AT003 bypassed | Binary
102 | DI_bypassed_804 | 28311 | 104540 | 10HCB18 AT004 bypassed | Binary
103 | DI_bypassed_805 | 28312 | 104541 | 10HCB18 AT005 bypassed | Binary
104 | DI_bypassed_806 | 28313 | 104542 | 10HCB18 AT006 bypassed | Binary
105 | DI_bypassed_807 | 28314 | 104543 | 10HCB18 AT007 bypassed | Binary
106 | DI_bypassed_808 | 28315 | 104544 | 10HCB18 AT008 bypassed | Binary
107 | DI_bypassed_809 | 28400 | 104545 | 10HCB18 AT009 bypassed | Binary
108 | DI_bypassed_810 | 28401 | 104546 | 10HCB18 AT010 bypassed | Binary
109 | DI_bypassed_811 | 28402 | 104547 | 10HCB18 AT011 bypassed | Binary
110 | DI_bypassed_812 | 28403 | 104548 | 10HCB18 AT012 bypassed | Binary
111 | DI_bypassed_813 | 28404 | 104549 | 10HCB18 AT013 bypassed | Binary
112 | DI_bypassed_601 | 28405 | 104550 | 10HCB16 AT001 bypassed | Binary
113 | DI_bypassed_602 | 28406 | 104551 | 10HCB16 AT002 bypassed | Binary
114 | DI_bypassed_603 | 28407 | 104552 | 10HCB16 AT003 bypassed | Binary
115 | DI_bypassed_604 | 28408 | 104553 | 10HCB16 AT004 bypassed | Binary
116 | DI_bypassed_902 | 28409 | 104554 | 10HCB19 AT002 bypassed | Binary
CONTROL STATUS
1 | DI_HMIcontrol | 28500 | 104561 | LocHMI/DCS | Binary
2 | DI_Single | 28501 | 104562 | Single/Double | Binary
3 | DI_MPRun | 28502 | 104563 | BOILER SOOT BLOWER CONTROL SYSTEM RUN | Binary
4 | DI_AHPRun | 28503 | 104564 | AH SOOT BLOWER CONTROL SYSTEM RUN | Binary
5 | DI_Pause | 28504 | 104565 | Main soot blower program paused | Binary
6 | DI_PH1 | 28505 | 104566 | SB STM PRES H | Binary
7 | DI_PL1 | 28506 | 104567 | SB STM PRES L | Binary
8 | DI_T1 | 28507 | 104568 | No.1 DRAIN TEMP H | Binary
9 | DI_T2 | 28508 | 104569 | No.2 DRAIN TEMP H | Binary
10 | DI_T1 | 28509 | 104570 | No.3 DRAIN TEMP H | Binary
11 | DI_T2 | 28510 | 104571 | No.4 DRAIN TEMP H | Binary
12 | DI_T2 | 28511 | 104572 | No.5 DRAIN TEMP H | Binary
13 | DI_G1 | 28512 | 104573 | One of GRP HCB13,11 SB advance | Binary
14 | DI_E1 | 28513 | 104574 | One of GRP HCB13,11 SB retract | Binary
15 | DI_H1 | 28514 | 104575 | One of GRP HCB13,11 SB overload | Binary
16 | DI_G3 | 28515 | 104576 | One of GRP HCB17,15 SB advance | Binary
17 | DI_E3 | 28600 | 104577 | One of GRP HCB17,15 SB retract | Binary
18 | DI_H3 | 28601 | 104578 | One of GRP HCB17,15 SB overload | Binary
19 | DI_G5 | 28602 | 104579 | One of GRP HCB19 AT001 advance | Binary
20 | DI_E5 | 28603 | 104580 | One of GRP HCB19 AT001 retract | Binary
21 | DI_H5 | 28604 | 104581 | One of GRP HCB19 AT001 overload | Binary
22 | DI_G2 | 28605 | 104582 | One of GRP HCB14,12 SB advance | Binary
23 | DI_E2 | 28606 | 104583 | One of GRP HCB14,12 SB retract | Binary
24 | DI_H2 | 28607 | 104584 | One of GRP HCB14,12 SB overload | Binary
25 | DI_G4 | 28608 | 104585 | One of GRP HCB18,16 SB advance | Binary
26 | DI_E4 | 28609 | 104586 | One of GRP HCB18,16 SB retract | Binary
27 | DI_H4 | 28610 | 104587 | One of GRP HCB18,16 SB overload | Binary
28 | DI_G6 | 28611 | 104588 | One of GRP HCB19 AT002 advance | Binary
29 | DI_E6 | 28612 | 104589 | One of GRP HCB19 AT002 retract | Binary
30 | DI_H6 | 28613 | 104590 | One of GRP HCB19 AT002 overload | Binary
31 | DI_LKSV1 | 28614 | 104591 | BLR SB PRES CRTL-V OPND | Binary
32 | DI_LKSV2 | 28615 | 104592 | BLR SB TEMP CRTL-V OPND | Binary
33 | DI_LK1 | 28700 | 104593 | MAIN SB STM VLV OPND | Binary
34 | DI_LG1 | 28701 | 104594 | MAIN SB STM VLV CLSD | Binary
35 | DI_HF1 | 28702 | 104595 | MAIN SB STM VLV FAULT | Binary
36 | DI_LK2 | 28703 | 104596 | SB SPRAY WATER VLV OPND | Binary
37 | DI_LG2 | 28704 | 104597 | SB SPRAY WATER VLV CLSD | Binary
38 | DI_HF2 | 28705 | 104598 | SB SPRAY WATER VLV FAULT | Binary
39 | DI_LK3 | 28706 | 104599 | AUX SB STM VLV OPND | Binary
40 | DI_LG3 | 28707 | 104600 | AUX SB STM VLV CLSD | Binary
41 | DI_HF3 | 28708 | 104601 | AUX SB STM VLV FAULT | Binary
42 | DI_LK4 | 28709 | 104602 | No.1 DRAIN VLV OPND | Binary
43 | DI_LG4 | 28710 | 104603 | No.1 DRAIN VLV CLSD | Binary
44 | DI_HF4 | 28711 | 104604 | No.1 DRAIN VLV FAULT | Binary
45 | DI_LK5 | 28712 | 104605 | No.2 DRAIN VLV OPND | Binary
46 | DI_LG5 | 28713 | 104606 | No.2 DRAIN VLV CLSD | Binary
47 | DI_HF5 | 28714 | 104607 | No.2 DRAIN VLV FAULT | Binary
48 | DI_LK6 | 28715 | 104608 | No.3 DRAIN VLV OPND | Binary
49 | DI_LG6 | 28800 | 104609 | No.3 DRAIN VLV CLSD | Binary
50 | DI_HF6 | 28801 | 104610 | No.3 DRAIN VLV FAULT | Binary
51 | DI_LK7 | 28802 | 104611 | No.4 DRAIN VLV OPND | Binary
52 | DI_LG7 | 28803 | 104612 | No.4 DRAIN VLV CLSD | Binary
53 | DI_HF7 | 28804 | 104613 | No.4 DRAIN VLV FAULT | Binary
54 | DI_LK8 | 28805 | 104614 | No.5 DRAIN VLV OPND | Binary
55 | DI_LG8 | 28806 | 104615 | No.5 DRAIN VLV CLSD | Binary
56 | DI_HF8 | 28807 | 104616 | No.5 DRAIN VLV FAULT | Binary
57 | DI_StartFail1 | 28808 | 104617 | One of GRP HCB13,11 SB start failure | Binary
58 | DI_StartFail3 | 28809 | 104618 | One of GRP HCB17,15 SB start failure | Binary
59 | DI_StartFail5 | 28810 | 104619 | One of GRP HCB19AT001 start failure | Binary
60 | DI_StartFail2 | 28811 | 104620 | One of GRP HCB14,12 SB start failure | Binary
61 | DI_StartFail4 | 28812 | 104621 | One of GRP HCB18,16 SB start failure | Binary
62 | DI_StartFail6 | 28813 | 104622 | One of GRP HCB19AT002 start failure | Binary
63 | DI_DM | 28814 | 104623 | Soot blower control system simulate | Binary
64 | DI_LF_L | 28815 | 104624 | LFT SIDE SB STM FLW L | Binary
65 | DI_LF_R | 28900 | 104625 | RHT SIDE SB STM FLW L | Binary

## RULES
Optimization Cycle Steps:
1) Check Area, Zone and Blower Eligibility
2) Determine if an eligible Zone needs cleaning (using rules and/or numerical models)
3) Determine what eligible Blower in the selected Zone to run (using rules and/or numerical models)
4) Send request to SBCS
5) Wait, Repeat
Zones : |  | Area Group | Area Code | Seq.Rank | Rules Description | Tags | Rules | Unit | Lim.H | Lim.L
1)Furnace Area
| - Zone Front Wall | 100 | 101 s/d 120 | 1 | SH 2ND SPRAY WTR FLOW L | FT1A010601_PNT | > | t/h |  |  | 1
| - Zone Left Wall | 300 | 301 s/d 320 | 3 | SH 2ND SPRAY WTR FLOW R | FT1A011204_PNT | > | t/h |  |  | 0
| - Zone Right Wall | 400 | 401 s/d 420 | 4
| - Zone Back Wall | 200 | 201 s/d 220 | 2
2)Convection Area
| - Zone SHP (LEFT) | 700 | 701 | 7 | SH 1ST SPRAY WATER FLOW L | FT1A010503_PNT | > | t/h | 14.5 |  | 1
| - Zone RHP (LEFT) | 700 | 702 s/d 704 | 7 | PLATEN SH 2ND SPRAY OUT STM TEMP L |  | > | ⁰C | 395.5 |  | 1
| - Zone RHF (LEFT) | 700 | 705 s/d 706 | 7
| - Zone SHF (LEFT) | 700 | 707 s/d 708 | 7
| - Zone VERT. LTSH (LEFT) | 700 | 709 | 7
| - Zone S.HOR LTSH (LEFT) | 700 | 710 s/d 711 | 7
| - Zone P.HOR LTSH (LEFT) | 700 | 712 s/d 713 | 7
| - Zone S. ECO (LEFT) | 500 | 501 s/d 502 | 5 | LMTD Eco Left |  | > | ⁰C | 112 | 101 | 0
| - Zone P. ECO (LEFT) | 500 | 503 s/d 504 | 5
| - Zone SHP (RIGHT) | 800 | 801 | 8 | SH 1ST SPRAY WATER FLOW R |  | > | t/h | 18.5 |  | 0
| - Zone RHP (RIGHT) | 800 | 802 s/d 804 | 8 | PLATEN SH 2ND SPRAY OUT STM TEMP R |  | > | ⁰C | 468.7
| - Zone RHF (RIGHT) | 800 | 805 s/d 806 | 8
| - Zone SHF (RIGHT) | 800 | 807 s/d 808 | 8
| - Zone VERT. LTSH (RIGHT) | 800 | 809 | 8
| - Zone S.HOR LTSH (RIGHT) | 800 | 810 s/d 811 | 8
| - Zone P.HOR LTSH (RIGHT) | 800 | 812 s/d 813 | 8
| - Zone S. ECO (RIGHT) | 600 | 601 s/d 602 | 6 | LMTD Eco right |  | > | ⁰C | 120 | 112 | 1
| - Zone P. ECO (RIGHT) | 600 | 603 s/d 604 | 6
3)Air Heater Area
| - Zone AH (LEFT) | 900 | 901 | 9 | No1 APH OUTLET FLUE GAS TEMP |  | > | ⁰C |  |  | 1
| - ZoneAH (RIGHT) | 900 | 902 | 9 | No2 APH OUTLET FLUE GAS TEMP |  | > | ⁰C |  |  | 1

## Ref.Val
|  |  | Temperature in °F | [5 empty] | Temperature in °C
Clause | Definition | Unit | Typical Value | Above | Below | Eligibility | Selection | Unit | Typical Value | Above | Below
SootOptON | SootOptMode > LogicalTrue |  | 1 | 0.5 |  | x
MW OK | GrossMW > MW Cutoff | MW | 492.7 | 100 |  | x
StartOK_IKN | IKsActiveN < Th_IKsActiveN |  | 0 |  | 1 | x
StartOK_IKS | IKsActiveS < Th_IKsActiveS |  | 0 |  | 1 | x
StartOK_IR | IRsActive < Th_IRsActive |  | 0 |  | 1 | x
ArchActive | AnyArchBlower > LogicalTrue |  | 0 | 0.5 |  | x
SHRHdeltaLoLo | SHRHdelta < Th_SHRHdeltaLoLo | deltaF | -24.3 |  | -70 | x |  |  | -13.5 |  | -38.8889
FSH North Active | IKSHActiveN = Th_IKsActiveN |  | 0 | 1 | 1 | x
FSH South Active | IKSHActiveS = Th_IKsActiveS |  | 0 | 1 | 1 | x
Allow_TS_Rules | Delayed_Enable > LogicalTrue |  | 1 | 0.5 |  |  | x
UseProcessRules | UseProcessRules > LogicalTrue |  | 1 | 0.5 |  |  | x
UseEfficiencyRules | UseEfficiencyRules > LogicalTrue |  | 1 | 0.5 |  |  | x
N SH T HiHi | N SH T > Th_N SH T HiHi | degF | 995.7 | 1012 |  |  | x | degC | 553.1667 | 562.2222
N SH T Hi | N SH T > Th_N SH T Hi | degF | 995.7 | 1007 |  |  | x | degC | 553.1667 | 559.4444
N SH T Lo | N SH T < Th_N SH T Lo | degF | 995.7 |  | 997 |  | x | degC | 553.1667 |  | 553.8889
N SH T LoLo | N SH T < Th_N SH T LoLo | degF | 995.7 |  | 992 |  | x | degC | 553.1667 |  | 551.1111
N RH T HiHi | N RH T > Th_RH T HiHi | degF | 972.5 | 988.8 |  |  | x | degC | 540.2778 | 549.3333
N RH T Hi | N RH T > Th_RH T Hi | degF | 972.5 | 983.8 |  |  | x | degC | 540.2778 | 546.5556
N RH T Lo | N RH T < Th_RH T Lo | degF | 972.5 |  | 973.8 |  | x | degC | 540.2778 |  | 541
N RH T LoLo | N RH T < Th_RH T LoLo | degF | 972.5 |  | 968.8 |  | x | degC | 540.2778 |  | 538.2222
S SH T HiHi | S SH T > Th_S SH T HiHi | degF | 995.3 | 1007 |  |  | x | degC | 552.9444 | 559.4444
S SH T Hi | S SH T > Th_S SH T Hi | degF | 995.3 | 1007 |  |  | x | degC | 552.9444 | 559.4444
S SH T Lo | S SH T < Th_S SH T Lo | degF | 995.3 |  | 997 |  | x | degC | 552.9444 |  | 553.8889
S SH T LoLo | S SH T < Th_S SH T LoLo | degF | 995.3 |  | 992 |  | x | degC | 552.9444 |  | 551.1111
S RH T HiHi | S RH T > Th_RH T HiHi | degF | 971 | 988.8 |  |  | x | degC | 539.4444 | 549.3333
S RH T Hi | S RH T > Th_RH T Hi | degF | 971 | 983.8 |  |  | x | degC | 539.4444 | 546.5556
S RH T Lo | S RH T < Th_RH T Lo | degF | 971 |  | 973.8 |  | x |  | 539.4444 |  | 541
S RH T LoLo | S RH T < Th_RH T LoLo | degF | 971 |  | 968.8 |  | x |  | 539.4444 |  | 538.2222
SH Spray Auto | SH Spray Mode > LogicalTrue |  | 1 | 0.5 |  |  | x
SH Spray Hi | SH Spray Flow > Th_SH Spray Hi | klb/h | 0.3 | 100 |  |  | x | ton/h | 0.13608 | 45.3592
RH Spray Auto | RH Spray Mode > LogicalTrue |  | 0 | 0.5 |  |  | x
RH Spray Hi | RH Spray Flow > Th_RH Spray Hi | klb/h | 0 | 5 |  |  | x | ton/h | 0 | 2.268
SH Spray S Hi | SH Spray Flow S > Th_SH Spray Hi | klb/h | 0 | 100 |  |  | x | ton/h | 0 | 45.3592
SHSpray N Hi | SH Spray Flow N > Th_SH Spray Hi | klb/h | 0.6 | 100 |  |  | x | ton/h | 0.27216 | 45.3592
SH Spray N Lo | SH Spray Flow N < Th_SH Spray Lo | klb/h | 0.6 |  | 10 |  | x | ton/h | 0.27216 |  | 4.5359
SH Spray S Lo | SH Spray Flow S < Th_SH Spray Lo | klb/h | 0 |  | 10 |  | x | ton/h | 0 |  | 4.5359
N APH GasIn T Hi | N APHGasInlT > Th_N APHGasInTempHi | degF | 644.4 | 675.6 |  |  | x | degC | 358 | 375.3333
S APH GasIn T Hi | S APHGasInT > Th_S APHGasInTempHi | degF | 669 | 675.6 |  |  | x | degC | 371.6667 | 375.3333
SHRHdeltaLo | SHRHdelta < Th_SHRHdeltaLo | deltaF | -24.3 |  | -60 |  | x | degC | -13.5 |  | -33.3333
SH Spray L N Hi | SHN_Lwr_LoRngVlvPos > TH_SH Spray Vlv Hi | % | -0.6 | 70 |  |  | x
SH Spray L S Hi | SHS_Lwr_LoRngVlvPos > TH_SH Spray Vlv Hi | % | -0.4 | 70 |  |  | x
SH Spray U N Hi | SHN_Upper_VlvPos > TH_SH Spray Vlv Hi | % | -0.2 | 70 |  |  | x
SH Spray U S Hi | SHS_Upper_VlvPos > TH_SH Spray Vlv Hi | % | -0.9 | 70 |  |  | x
SH Spray L N Lo | SHN_Lwr_LoRngVlvPos < TH_SH Spray Vlv Lo | % | -0.6 |  | 20 |  | x
SH Spray L S Lo | SHS_Lwr_LoRngVlvPos < TH_SH Spray Vlv Lo | % | -0.4 |  | 20 |  | x
SH Spray U N Lo | SHN_Upper_VlvPos < TH_SH Spray Vlv Lo | % | -0.2 |  | 20 |  | x
SH Spray U S Lo | SHS_Upper_VlvPos < TH_SH Spray Vlv Lo | % | -0.9 |  | 20 |  | x